## CCCEZE
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
CCCEZE: Control Conjunto | [5 empty] | ¦ Generador: |  |  | Fecha: | Julio 2011
Modelo escrito por el Usuario: Compensadores Síncronos de Ezeiza
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
CONs | # |  | Value | Description
J |  |  | 1.02 | VREFMAX, Maximum of Reference Voltage
J+1 |  |  | 0.98 | VREFMIN, Minimum of Reference Voltage
J+2 |  |  | 0.000125 | S, Slope of changes for Reference Voltage
J+3 |  |  | 1.1 | VMMAX, Maximun of Measured Voltage
J+4 |  |  | 0.9 | VMMIN, Minimun of Measured Voltage
J+5 |  |  | 14.4 | KP, Proportional Gain of PI Controller
J+6 |  |  | 0.2 | 1/TN, Integral Time of PI Controller
J+7 |  |  | 1 | QREFMAX, Maximum Output of PI Controller
J+8 |  |  | -0.96 | QREFMIN, Minimum Output of PI Controller
J+9 |  |  | 0.02 | Tt, Time of Measured Voltage Trasducer
ICONs | # |  | Value | Description
M |  |  | 3000 | IB, BUS of Controlled Voltage
M+1 |  |  | 3651 | IBUS1, BUS of Compensator Number 1
M+2 |  |  | '1 ' | IM1, Index Machine of Compensator Number 1
M+3 |  |  | 755 | ICON1, ICON Number of Switch V/Q for UNITROLF of Compensator Number 1
M+4 |  |  | 1290 | VAR1, VAR Number of QRef for UNITROLF of Compensator Number 1
M+5 |  |  | 3652 | IBUS2, BUS of Compensator Number 2
M+6 |  |  | '2 ' | IM2, Index Machine of Compensator Number 2
M+7 |  |  | 763 | ICON2, ICON Number of Switch V/Q for UNITROLF of Compensator Number 2
M+8 |  |  | 1323 | VAR2, VAR Number of QRef for UNITROLF of Compensator Number 2
M+9 |  |  | 3653 | IBUS3, BUS of Compensator Number 3
M+10 |  |  | '3 ' | IM3, Index Machine of Compensator Number 3
M+11 |  |  | 771 | ICON3, ICON Number of Switch V/Q for UNITROLF of Compensator Number 3
M+12 |  |  | 1356 | VAR3, VAR Number of QRef for UNITROLF of Compensator Number 3
M+13 |  |  | 3654 | IBUS4, BUS of Compensator Number 4
M+14 |  |  | '4 ' | IM4, Index Machine of Compensator Number 4
M+15 |  |  | 779 | ICON4, ICON Number of Switch V/Q for UNITROLF of Compensator Number 4
M+16 |  |  | 1389 | VAR4, VAR Number of QRef for UNITROLF of Compensator Number 4
M+17 |  |  | 3655 | IBUS5, BUS of Compensator Number 5
M+18 |  |  | '5 ' | IM5, Index Machine of Compensator Number 5
M+19 |  |  | 787 | ICON5, ICON Number of Switch V/Q for UNITROLF of Compensator Number 5
M+20 |  |  | 1422 | VAR5, VAR Number of QRef for UNITROLF of Compensator Number 5
M+21 |  |  | 3656 | IBUS6, BUS of Compensator Number 6
M+22 |  |  | '6 ' | IM6, Index Machine of Compensator Number 6
M+23 |  |  | 795 | ICON6, ICON Number of Switch V/Q for UNITROLF of Compensator Number 6
M+24 |  |  | 1455 | VAR6, VAR Number of QRef for UNITROLF of Compensator Number 6
STATEs | # |  | Description |  |  | VARs | # | Description
K |  |  | Voltage Reference Integer |  |  | L |  | VREFEXT, External Reference Voltage
K+1 |  |  | PI Controller Integer |  |  | L+1 |  | VMLIM, Limited Measured Voltage
K+2 |  |  | Measured Voltage Trasducer |  |  | L+2 |  | VP, Proportional Output of PI Controller
[6 empty] | L+3 |  | VI, Integral Output of PI Controller
IBUS, ‘USRMDL’, ID, ’CCCEZE’, 8, 0, 25, 10, 3, 6, | [5 empty] | L+4 |  | NCSCC, Number of Compensator connected
ICON(M) to ICON(M+24), CON(J) to CON(J+9) /
[6 empty] | L+5 |  | VPI, Output of PI Controller
Diagrama de Bloques
CCCEZE
VREF
QREF
VMEASURED