## DC4OEL
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
DC4OEL: Maximum Excitation Limiter Model Data Sheets | [5 empty] | ¦ Generador: |  |  | Fecha: |  | Marzo 2012
Modelo escrito por el Usuario
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
CONs | # |  | Value | Description |  |  | STATEs | # |  | Description
J |  |  |  | TR_OEL |  |  | K |  |  | Measured IFD
J+1 |  |  |  | KG_OEL |  |  | K+1 |  |  | IFD Integral Controller Output
J+2 |  |  |  | KI_OEL
J+3 |  |  |  | VMN_OEL or Zero(1) |  |  | K+2 |  |  | Measured ITERM
J+4 |  |  |  | IFDNOM Base Field Current [pu] |  |  | K+3 |  |  | ITERM Integral Controller Output
J+5 |  |  |  | IFD1 High Limit, in pu of IFDNOM
J+6 |  |  |  | TO1 Permissible Time for IFD1
J+7 |  |  |  | IFD2 Medium Limit, in pu of IFDNOM |  |  | VARs | # |  | Description
J+8 |  |  |  | TO2 Permissible Time for IFD2 |  |  | L |  |  | OEL_Ref
J+9 |  |  |  | IFD3 Steady State Limit, in pu of IFDNOM |  |  | L+1 |  |  | OEL Output
J+10 |  |  |  | TO3 Reset Time |  |  | L+2 |  |  | OEL Timer Memory
J+11 |  |  |  | TR_SCL |  |  | L+3 |  |  | SCL_Ref
J+12 |  |  |  | KG_SCL |  |  | L+4 |  |  | SCL Outpu
J+13 |  |  |  | KI_SCL |  |  | L+5 |  |  | SCL Timer Memory
J+14 |  |  |  | VMX_SCL |  |  | L+6 |  |  | SCL Maximum Limit
J+15 |  |  |  | VMN_SCL |  |  | L+7 |  |  | SCL Minimum Limit
J+16 |  |  |  | TSD Delay Time
J+17 |  |  |  | ISC1 High Limit in pu of MBASE |  |  | IBUS, ‘USRMDL’, ID, ’DC4OEL’, 10, 0, 8,
J+18 |  |  |  | TS1 Permissible Time for ISCL |  |  | 21, 4, 8, ICON(M) to ICON(M+7),
J+19 |  |  |  | ISC2 Steady State Limit in pu of MBASE |  |  | CON(J) to CON(J+20) /
J+20 |  |  |  | TS2 Reset Time
ICONs | # |  | Value | Description
M |  |  |  | Switch ON/OFF OEL (1: On, 0: OFF)(2)
M+1 |  |  |  | Switch ON/OFF SCL (1: On, 0: OFF)(3)
M+2 |  |  |  | Delay Flag OEL
M+3 |  |  |  | Time Out Flag OEL
M+4 |  |  |  | Timer Status OEL
M+5 |  |  |  | Delay Flag SCL
M+6 |  |  |  | Time Out Flag SCL
M+7 |  |  |  | Timer Status SCL
Notes:
(1): When VMN_OEL is zero, it takes -VREF (Excitation System Reference) as Minimum Limit.
(2): When ICON(M) is zero, the OEL Limiter is inactive, but if ICON(M) is 1 it is active.
(3): When ICON(M+1) is zero, the SCL Limiter is inactive, but if ICON(M+1) is 1 it is active.
Diagrama de Bloques
Notes:
When QGEN is ≥0 (lagging power factor) SignQ is 1, and when QGEN is <0 it takes a value of -1.
To is the time after of which the respective limiters become inactive. This condition is produced when the last timer (TO3 or TS2) is time out, and the respective Limiter Output is zero. When the limiters are becoming inactive, the References (OEL_REF or SCL_REF) take their highest value.
When SCL is inactive it takes as reference 10 pu, but if TSD is cero, it takes as reference ISCL1.
DC4OEL
ITERM
VOEL
XadIFD