## DC4UEL
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
DC4UEL: Minimum Excitation Limiter Model Data Sheets | [6 empty] | ¦ Generador: |  |  | Fecha: | Marzo 2012
Modelo escrito por el Usuario
This model is located at system bus | [5 empty] | IBUS
Machine identifier | [5 empty] | ID
This model uses CONs starting with | [5 empty] | J
and STATEs starting with | [5 empty] | K
and VARs starting with | [5 empty] | L
and ICONs starting with | [5 empty] | M
CONs | # |  | Value | Description |  |  |  | VARs | # | Description
J |  |  |  | TR |  |  |  | L |  | QUEL_REF
J+1 |  |  |  | TUEL |  |  |  | L+1 |  | VC Controller Output
J+2 |  |  |  | KUEL |  |  |  | L+2 |  | VTK
J+3 |  |  |  | Kl |  |  |  | L+3 |  | PGEN/VTK
J+4 |  |  |  | KUELMX or Zero(1) |  |  |  | L+4 |  | Output Q = f(PFLT)
J+5 |  |  |  | FCTP Power Coeficient
J+6 |  |  |  | QBIAS >0, ¦QGEN¦ at Zero Lead Power Factor
J+7 |  |  |  | K Terminal Voltage Exponent(3) |  |  |  | STATEs | # | Description
J+8 |  |  |  | P1 | Points of Q = f(P) straight lines function |  |  | K |  | Measured QGEN
J+9 |  |  |  | Q1 |  |  |  | K+1 |  | Filtered ETERM
J+10 |  |  |  | P2 |  |  |  | K+2 |  | Filtered PGEN/VTK
J+11 |  |  |  | Q2 |  |  |  | K+3 |  | Integral Controller Output
J+12 |  |  |  | P3
J+13 |  |  |  | Q3 |  |  |  | IBUS, ‘USRMDL’, ID, ’DC4UEL’, 9, 0, 1, 18, 4, 5,
J+14 |  |  |  | P4 |  |  |  | ICON(M), CON(J) to CON(J+17) /
J+15 |  |  |  | Q4
J+16 |  |  |  | P5
J+17 |  |  |  | Q5
ICONs | # |  | Value | Description
M |  |  |  | Switch UEL Mode (0 or 1)(2)
Notes:
(1): When VUELMX is zero, it takes -0.5*VREF (Excitation System Reference) as Maximum Limit.
(2): When ICON(M) is 0, QUEL_REF = (FCTP*P2–1)*QBIAS; if ICON(M)=1, then QUEL_REF is calculated
from QUEL_Ref = f(P) Multiple Straight Lines Segment Function.
(3) When K exponent is zero, the terminal voltage is assumed as constant and equal to 1 pu.
Diagrama de Bloques
Notes:
About Straight Lines Function: When P <P1, Q=Q1 and when P >P5, Q=Q5.
DC4UEL
ETERM
PELEC
VUEL
QELEC