## EX2000
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
EX2000: Excitation System Model Data Sheets | [5 empty] | Generador: |  |  |  | Fecha: | Julio 2011
EX2000 Excitation System also represents IEEE Type AC7B Alternator-Rectifier Excitation System (Under Excitation Limiter is not included)
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VAR |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
STATEs | # |  | Description |  |  |  | VAR | # | Description
K |  |  | Voltage Transducer |  |  |  | L |  | Inverse Timing Function Memory
K+1 |  |  | 1st PI controller | [5 empty] | <1: Latch Gate 2 signal is 0
K+2 |  |  | 2nd PI controller | [5 empty] | ≥1: Latch Gate 2 signal is 1
K+3 |  |  | Exciter field voltage
K+4 |  |  | 3rd PI controller (Field Current Limiter)
K+5 |  |  | Lead-lag element (Field Voltage Limiter)
ICONs | # |  | Value | Description
M |  |  |  | 0: Field Current Limiter is excluded (and upper limit VEMAX is on)
1: Field Current Limiter is included (and upper limit VEMAX is off)
M+1 |  |  |  | 0: Minimum Gate 2 is excluded.
1: Minimum Gate 2 is included.
M+2 |  |  |  | Memory. Set to 0.
0: Latch Gate 1 signal is 0
1: Latch Gate 1 signal is 1
M+3 |  |  |  | Memory. Set to 0.
0: Field Current Limiter Timer is not active
1: Field Current Limiter Timer is active
IBUS, ’EX2000’, ID, ICON(M), ICON(M+1), CON(J) to CON(J+44) /
CONs | # |  | Value | Description
J |  |  |  | KPR, proportional gain
J+1 |  |  |  | KIR, integral gain
J+2 |  |  |  | VRMAX, maximum output
J+3 |  |  |  | VRMIN, minimum output
J+4 |  |  |  | KPA, proportional gain
J+5 |  |  |  | KIA, integral gain
J+6 |  |  |  | VAMAX, maximum output
J+7 |  |  |  | VAMIN, minimum output
J+8 |  |  |  | KP, constant
J+9 |  |  |  | KL, constant
J+10 |  |  |  | TE, exciter field time constant (sec)
J+11 |  |  |  | VFEMAX, parameter of VEMAX, exciter field maximum output
J+12 |  |  |  | KE, exciter field proportional constant
J+13 |  |  |  | KC, rectifier regulation factor
J+14 |  |  |  | KD, exciter regulation factor
J+15 |  |  |  | KF1
J+16 |  |  |  | KF2
J+17 |  |  |  | E1, exciter flux at knee of curve
J+18 |  |  |  | S(E1), saturation factor at knee of curve
J+19 |  |  |  | E2, maximum exciter flux
J+20 |  |  |  | S(E2), saturation factor at maximum exciter flux
J+21 |  |  |  | KVHZ, Volt/Hz gain
J+22 |  |  |  | KRCC, Volt/reactive current gain
J+23 |  |  |  | TR, voltage transducer time constant (sec)
J+24 |  |  |  | IFDREF1, field current 1st reference
J+25 |  |  |  | IFDFEF2, field current 2nd
J+26 |  |  |  | IFDREF3, field current 3rd reference
J+27 |  |  |  | IFDREF4, field current 4th reference
J+28 |  |  |  | I1, inverse timing constant
J+29 |  |  |  | T1, inverse timing constant (sec)
J+30 |  |  |  | I2, inverse timing constant
J+31 |  |  |  | T2, inverse timing constant (sec)
J+32 |  |  |  | I3, inverse timing constant
J+33 |  |  |  | T3, inverse timing constant (sec)
J+34 |  |  |  | I4, inverse timing constant
J+35 |  |  |  | T4, inverse timing constant (sec)
J+36 |  |  |  | TLEAD, field current limiter time constant (sec)
J+37 |  |  |  | TLAG, field current limiter time constant (sec)
J+38 |  |  |  | KPIFD, proportional gain
J+39 |  |  |  | KIIFD, integral gain
J+40 |  |  |  | IFDLIMP, maximum output
J+41 |  |  |  | IFDLIMN, minimum output
J+42 |  |  |  | IFDADVLIM, advance field current limit
J+43 |  |  |  | VEMIN, exciter field minimum output
J+44 |  |  |  | REFLIMP, voltage reference signal limit
The values are given in per unit unless the unit is shown. For field current references and inverse timing constants the value of the current is in per unit of the generator Air Gap Line base.
Diagrama de Bloques
To represent IEEE Type AC7B System you need to set KVHZ = 0 and KRCC = 0, to set ICON(M+1) = 0 (to exclude Minimum Gate 2) and to set TR = 0 (to exclude the Voltage Transducer).
To represent IEEE Type AC7B System you need to set ICON(M) = 0 (to exclude this limiter).