## EXF2
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
EXF2: Wind Energy Converter Model Data Sheets | [7 empty] | ¦ Generador: |  | Fecha: | Mayo 2012
Modelo escrito por el Usuario: ENERCON Wind Energy Converter (WEC) Model ExF2
This model is located at system bus | [5 empty] | IBUS
Machine identifier | [5 empty] | ID
This model uses CONs starting with | [5 empty] | J
and VARs starting with | [5 empty] | L
and ICONs starting with | [5 empty] | M
CONs | # |  | Value | Default | Range |  | Description
J | [6 empty] | Prat |  | Rated power of one WEC, [kW]
J+1 | [6 empty] | Imax |  | Short circuit current Ik”,MAX of one WEC, [A]
J+2 | [6 empty] | QMAX_EXP |  | Max. reactive power export, [pu of Prat]
J+3 | [6 empty] | QMAX_IMP |  | Max. reactive power import, [pu of Prat]
J+4 |  |  |  | 0.8 | 0.8 - 0.95 |  | U_UVP1 |  | Threshold value for undervoltage detection, [pu]
J+5 |  |  |  | 0.8 | 0.8 - 0.95 |  | U_SL_UVRT |  | Threshold value for undervoltage clearance detection, [pu]
J+6 |  |  |  | 5 | 0.05 - 5 |  | TD_UVRT |  | Maximum UVRT time, [s]
J+7 |  |  |  | 1.2 | 1.0 - 1.2 |  | U_OVP2 |  | Threshold value for overvoltage detection, [pu]
J+8 |  |  |  | 1.2 | 1.0 - 1.2 |  | U_SL_OVRT |  | Threshold value for overvoltage clearance detection, [pu]
J+9 |  |  |  | 5 | 0.05 - 5 |  | TD_OVRT |  | Maximum OVRT time, [s]
J+10 |  |  |  | 1 | 0.1 - 3 |  | T_RAMP |  | ZPM: Current ramp time, [s]
J+11 |  |  |  | 0.5 | 0 - 1 |  | K_PAM |  | PAM: Reactive current factor, [-]
J+12 |  |  |  |  | 0 - 10 |  | K_QUM |  | QUM2: dQ/dU-Slope, [-]
J+13 |  |  |  | 52.00 62.00 | 50 - 57 60 - 67 |  | F_OF |  | Threshold value for overfrequency detection, [Hz]
J+14 |  |  |  | 0.07 | 0.07 - 60 |  | TD_OF |  | Overfrequency protection delay time, [s]
J+15 |  |  |  | 47.00 57.00 | 43 - 50 53 - 60 |  | F_UF |  | Threshold value for underfrequency detection, [Hz]
J+16 |  |  |  | 0.07 | 0.07 - 60 |  | TD_UF |  | Underfrequency protection delay time, [s]
J+17 |  |  |  |  | 0 - 50000 |  | KP1_FCU |  | Proportional gain 1, [-]
J+18 |  |  |  |  | 0 - 100 |  | KI1_FCU |  | Integral gain, [1/s]
J+19 |  |  |  |  | 0 - 500 |  | TD1_FCU |  | Time delay 1, [s]
J+20 |  |  |  |  | 0 - 100 |  | KP2_FCU |  | Proportional gain 2, [-]
J+21 |  |  |  |  | 0 - 500 |  | TD2_FCU |  | Time delay 2, [s]
J+22 |  |  |  |  | 0 - 1 |  | QMAX_EXP_POC |  | Max. reactive power export at controlled bus, [pu of NWEC*Prat]
J+23 |  |  |  |  | 0 - 1 |  | QMAX_IMP_POC |  | Max. reactive power import at controlled bus, [pu of NWEC*Prat]
J+24 |  |  |  |  | 0 - 1 |  | QREF_OFF |  | Reactive power offset, [pu of NWEC*Prat]
J+25 |  |  |  | 0.01 | 0 - 1 |  | TF1_FCU |  | Voltage filter time constant, [s]
J+26 |  |  |  | 0.01 | 0 - 1 |  | TF2_FCU |  | Power filter time constant, [s]
J+27 |  |  |  |  | 0 - 1 |  | U_RESET_UV |  | Lower threshold for output reset, [pu]
J+28 |  |  |  |  | 1 - 1.5 |  | U_RESET_OV |  | Upper threshold for output reset, [pu]
ICONs | # |  | Value | Description
M |  |  |  | Memory |  | Used by PSS/E
M+1 |  |  |  | NWEC |  | Number of WEC represented by the model
M+2 |  |  |  | STATCOM |  | STATCOM Option (0 = no, 1 = yes)
M+3 |  |  |  | FCU_MODE |  | = 0 No remote control (FCU off) = 1 Control Type 1 (Voltage Control) = 2 Control Type 2 (Voltage-droop Control) = 3 Control Type 3 (Reactive Power Control) = 4 Control Type 4 (Power Factor Control)
M+4 |  |  |  | UVRT_MODE |  | = 0 FD-Configuration = 1 FT/FTQ-Configuration with ZPM = 2 FT/FTQ-Configuration with PQM = 3 FT/FTQ-Configuration with PAM = 4 FT/FTQ-Configuration with QUM1 = 5 FT/FTQ-Configuration with QUM2
M+5 |  |  |  | F_BUS |  | “From Bus” – Bus Number
M+6 |  |  |  | C_BUS |  | “To Bus” – Bus Number (Controlled Bus)
VARs | # |  | Description
L |  |  | FCU reference value Uref for Control Type 1 and 2, [pu]
FCU reference value Qref for Control Type 3, [pu]
FCU reference value PFref for Control Type 4
Where PFref > 0: Reactive power export, PFref < 0: Reactive power import
L+1 |  |  | For internal use
…
L+3
L+4 |  |  | FCU command value Qref_FCU for Full Converter Control Model
L+5 |  |  | For internal use
…
L+8
L+9 |  |  | FCU internal reference value Qref for Control Type 2 and 4
L+10 |  |  | For internal use
…
L+59
IBUS, ‘USRMDL’, ID, EXF2’, 1, 1, 7, 29, 0, 60, ICON(M) to ICON(M+6), CON(J) to CON(J+28)/
Diagrama de Bloques
ExF2 Model – Structure
Structure of the FCU Model