## GAST2P
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
GAST2P: Turbine-Governor Model Data Sheets | [5 empty] | Generador: |  |  | Fecha: | Julio 2011
Gas Turbine Model
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
CONs | # |  | Value | Description
J |  |  |  | W, governor gain (1/droop) (on turbine rating)
J+1 |  |  |  | X (sec) governor lead time constant
J+2 |  |  |  | Y (sec) > 0 governor lag time constant
J+3 |  |  |  | Z, governor mode: 1 Droop, 0 ISO
J+4 |  |  |  | ETD (sec)
J+5 |  |  |  | TCD (sec) |  |  | IBUS, ‘USRMDL’,ID, ’GAST2P', 5, 0, 0, 31, 13, 4,
J+6 |  |  |  | TRATE Turbine Rating (MW) |  |  | CON(J) to CON(J+30) /
J+7 |  |  |  | T (sec)
J+8 |  |  |  | MAX (p.u.) Limit
J+9 |  |  |  | MIN (p.u.) Limit |  |  | STATEs | # | Description
J+10 |  |  |  | ECR (sec) |  |  | K |  | Speed governor
J+11 |  |  |  | K3 |  |  | K+1 |  | Valve positioner
J+12 |  |  |  | A > 0. Valve Positioner |  |  | K+2 |  | Fuel system
J+13 |  |  |  | B (sec) > 0. Valve Positioner |  |  | K+3 |  | Radiation shield
J+14 |  |  |  | C Valve Positioner |  |  | K+4 |  | Thermocouple
J+15 |  |  |  | tF (sec) > 0 |  |  | K+5 |  | Temperature control
J+16 |  |  |  | KF |  |  | K+6 |  | Gas turbine dynamics
J+17 |  |  |  | K5 |  |  | K+7 |  | Combustor
J+18 |  |  |  | K4 |  |  | K+8 |  | Combustor
J+19 |  |  |  | T3 (sec) > 0 |  |  | K+9 |  | Turbine/exhaust
J+20 |  |  |  | T4 (sec) > 0 |  |  | K+10 |  | Turbine/exhaust
J+21 |  |  |  | tT > 0 |  |  | K+11 |  | Fuel controller delay
J+22 |  |  |  | T5 (sec) > 0 |  |  | K+12 |  | Fuel controller delay
J+23 |  |  |  | AF1
J+24 |  |  |  | BF1 |  |  | VARs | # | Description
J+25 |  |  |  | AF2 |  |  | L |  | Governor reference
J+26 |  |  |  | BF2 |  |  | L+1 |  | Temperature reference flag
J+27 |  |  |  | CF2
J+28 |  |  |  | TR (degree), Rated Temp.1 |  |  | L+2 |  | Low value select output
J+29 |  |  |  | K6 (pu), Minimum fuel flow |  |  | L+3 |  | Output of temperature control
J+30 |  |  |  | TC (degree), Temp. control1
1 Units can be °F or °C depending on constants AF1 and BF1.
Diagrama de Bloques
GAST2P
SPEED
PMECH