## GEGT1
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
GEGT1: Turbine-Governor Model Data Sheets | [6 empty] | Generador: |  |  | Fecha: | Julio 2011
Modelo escrito por el Usuario
This model is located at system bus | [5 empty] | IBUS
Machine identifier | [5 empty] | ID
This model uses CONs starting with | [5 empty] | J
and STATEs starting with | [5 empty] | K
and VARs starting with | [5 empty] | L
CONs | # |  | Value |  | Description |  | STATEs | # | Description
J |  |  |  |  | PISO |  | K |  | Salida del Transductor de PELEC
J+1 |  |  |  |  | EPZ |  | K+1 |  | Salida del Governor
J+2 |  |  |  |  | TISO |  | K+2 |  | No utilizada
J+3 |  |  |  |  | ISOR |  | K+3 |  | Salida del control de Temperatura
J+4 |  |  |  |  | ZFHT |  | K+4 |  | Salida de la válvula de Combustible
J+5 |  |  |  |  | TREFSMPL |  | K+5 |  | Salida de la Turbina
J+6 |  |  |  |  | TBASE |  | K+6 |  | Derivada en el Control de Aceleración
J+7 |  |  |  |  | RPELEC |  | K+7 |  | Salida del sensor de Temperatura
J+8 |  |  |  |  | TPELEC |  | K+8 |  | Salida de Radiation Shield
J+9 |  |  |  |  | KPGOV |  | K+9 |  | IGV
J+10 |  |  |  |  | TGOV |  | K+10 |  | Sal. del Cntrl. de Temp. de los álabes
J+11 |  |  |  |  | KISOC |  | K+11 |  | Salida del Control de Aceleración
J+12 |  |  |  |  | TTEMP |  | K+12 |  | Gff
J+13 |  |  |  |  | KTEMP
J+14 |  |  |  |  | ASET |  | VARs | # | Description
J+15 |  |  |  |  | KA |  | L |  | fsrn
J+16 |  |  |  |  | TA |  | L+1 |  | fsrt
J+17 |  |  |  |  | WFNL |  | L+2 |  | fsra
J+18 |  |  |  |  | FSRMIN |  | L+3 |  | fsr
J+19 |  |  |  |  | TF |  | L+4 |  | tnr
J+20 |  |  |  |  | KTURB |  | L+5 |  | exhtt
J+21 |  |  |  |  | TTURB |  | L+6 |  | pm
J+22 |  |  |  |  | TTHCP |  | L+7 |  | cpr
J+23 |  |  |  |  | TNSHLD |  | L+8 |  | wf
J+24 |  |  |  |  | TDSHLD |  | L+9 |  | trf1
J+25 |  |  |  |  | IGVMAX |  | L+10 |  | trf2
J+26 |  |  |  |  | IGVMIN |  | L+11 |  | tbias
J+27 |  |  |  |  | KTIGV |  | L+12 |  | wa
J+28 |  |  |  |  | TTIGV |  | L+13 |  | mtmp
J+29 |  |  |  |  | TAIGV |  | L+14 |  | REFERENCE
J+30 |  |  |  |  | KGVFF |  | L+15 |  | INIT RATE LIMIT-TBIAS
J+31 |  |  |  |  | TGVFF |  | L+16 |  | INIT RATE LIMIT-TNR
J+32 |  |  |  |  | KFB |  | L+17 |  | INIT RATE LIMIT-TRF1
J+33 |  |  |  |  | FOBMAX |  | L+18 |  | PMECH
J+34 |  |  |  |  | RTBMAX
J+35 |  |  |  |  | RTBMIN |  | IBUS, ‘USRMDL’, ID, ’GEGT1’, 5, 0, 0, 64, 13, 19,
J+36 |  |  |  |  | RTMAX |  | CON(J) to CON(J+63) /
CONs continuación…
CONs | # |  | Value |  | Description
J+37 |  |  |  |  | RTMIN
J+38 |  |  |  |  | TREF1
J+39 |  |  |  |  | KCPR1
J+40 |  |  |  |  | TREF2
J+41 |  |  |  |  | KCPR2
J+42 |  |  |  |  | TREF3
J+43 |  |  |  |  | KCPR3
J+44 |  |  |  |  | TREF
J+45 |  |  |  |  | DBD
J+46 |  |  |  |  | EMAX
J+47 |  |  |  |  | RRMAX
J+48 |  |  |  |  | FLAG
J+49 |  |  |  |  | TAMB
J+50 |  |  |  |  | PAMB
J+51 |  |  |  |  | A0
J+52 |  |  |  |  | A1
J+53 |  |  |  |  | A2
J+54 |  |  |  |  | A3
J+55 |  |  |  |  | A4
J+56 |  |  |  |  | A5
J+57 |  |  |  |  | A6
J+58 |  |  |  |  | A7
J+59 |  |  |  |  | IGV0
J+60 |  |  |  |  | AF0
J+61 |  |  |  |  | KAF
J+62 |  |  |  |  | SBASE
J+63 |  |  |  |  | DBA
Detalle de las CONs
rpelec | Governor droop, per unit speed for one per unit electrical power
tpelec | Governor electrical power transducer time constant, sec
kpgov | Governor proportional gain
tgov | Governor PI controller lead time constant (kp/ki), sec
kisoc | Governor Isochronous reset time constant, sec
ttemp | Temperature controller lead time constant (kp/ki), sec
ktemp | Temperature controller proportional gain
aset | Acceleration controller limit setting, pu speed/sec
ka | Acceleration controller proportional gain
ta | Acceleration controller lead time constant (kp/ki), sec
wfnl | No load fuel flow, per unit
fsrmin | Minimum fuel valve, per unit
tf | Fuel valve time constant, sec
kturb | Turbine gain
tturb | Turbine time constant, sec
tthcp | Temperature detector (thermocouple) time constant, sec
tnshld | Radiation shield lead time constant, sec
tdshld | Radiation shield lag time constant, sec
igvmax | Maximum inlet guide vane opening, degrees
igvmin | Minimum inlet guide vane opening, degrees
ktigv | Guide vane temperature controller proportional gain
ttigv | Guide vane temperature controller lead time constant (Kp/Ki), sec
taigv | Guide vane actuator time constant, sec
kgvff | Governor guide vane feedforward gain
tgvff | Governor guide vane feedforward time constant, sec
kfb | Fuel override bias gain, degC per guide vane degree
fobmax | Maximum fuel override bias, degC
rtbmax | Maximum rate of change of temperature limit, degC per sec
rtbmin | Minimum rate of change of temperature limit, degC per sec
rtmax | Maximum rate of change of temperature reference, degC per sec
rtmin | Minimum rate of change of temperature reference, degC per sec
tref1 | Temperature limit control curve intercept, degC
kcpr1 | Temperature limit control curve slope, degC per unit Cpr
tref2 | Temperature reference control curve intercept, degC
kcpr2 | Temperature reference control curve slope, degC per unit Cpr
tref3 | Temperature reference control curve intercept, degC
kcpr3 | Temperature reference control curve slope, degC per unit Cpr
tref | Turbine control main reference (isotherm), degC
dbd | Governor dead band, per unit
emax | Governor error limit, per unit
rrmax | Maximum rate of change of load reference, per unit per sec
combc | Combined cycle flag
flag | Spare Flag
tamb | Ambient temperature, degC
pamb | Ambient pressure, degC
a0 | Compressor air flow coefficient
a1 | Compressor air flow coefficient
a2 | Compressor air flow coefficient
a3 | Temperature model coefficient
a4 | Temperature model coefficient
a5 | Pressure ratio model coefficient
a6 | Pressure ratio model coefficient
a7 | Pressure ratio model coefficient
igv0 | Guide vane / air flow model coefficient
kaf | Guide vane / air flow gain
Detalle de las VARs
fsrn | Salida del Control de Combustible, proveniente desde el governor, pu
fsrt | Salida del Control de Combustible, proveniente del Control de Temperatura, pu
fsra | Salida del Control de Combustible, proveniente del Control de Aceleración, pu
fsr | Salida del Control de Combustible seleccionada, pu
tnr | Referencia del Regulador, limitada por el Rate Limiter
exhtt | Temperatura de los gases de escape (=Tx)
pm | Potencia Mecánica de la Turbina, MW
cpr | Presión de la Turbina
wf | Flujo de Combustible
trf1 | Señal del Límite de Temperatura, °C
trf2 | Señal del Control de Temperatura, °C
tbias | Salida del Rate Limiter de Control de Temperatura
wa | Flujo de Aire, pu
mtmp | Temperatura Media de los gases de escape, °C
REFERENCE |  | Referencia del Regulador sin limitar
INIT RATE LIMIT-TBIAS |  |  |  | Variable interna del Rate Limit
INIT RATE LIMIT-TNR |  |  |  | Variable interna del Rate Limit
INIT RATE LIMIT-TRF1 |  |  |  | Variable interna del Rate Limit
PMECH | Potencia Mecánica
Diagrama de Bloques
GEGT1
PELEC
PMECH
