## GFT8WB
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
GFT8WB: Turbine-Governor Model Data Sheets | [5 empty] | Generador: |  |  | Fecha: | Diciembre 2015
Modelo escrito por el Usuario: Sistema de regulación de velocidad para Tgs aeroderivadas tipo Pratt&Whitney, con banda muerta
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
CONs | # |  | Value | Description
J |  |  |  | Kdroop - governor dropp (pu)
J+1 |  |  |  | Kpt1 - speed governor gain (pu)
J+2 |  |  |  | Tpt - speed governor time constant (sec)
J+3 |  |  |  | Kpt2 - speed governor integral action (=1:P+I, !=1:lead-lag)
J+4 |  |  |  | ETD - Turbine Exhaust delay (sec)
J+5 |  |  |  | TCD - Gas turbine dynamics (sec)
J+6 |  |  |  | TRATE - turbine rating (MW)
J+7 |  |  |  | T - Fuel Control delay (sec)
J+8 |  |  |  | MAX - limit (on turbine rating) (pu)
J+9 |  |  |  | MIN - limit (on turbine rating) (pu)
J+10 |  |  |  | ECR - Combustor delay (sec)
J+11 |  |  |  | K3 - Fuel control gain (pu)
J+12 |  |  |  | a - valve positioner gain (>0.0)
J+13 |  |  |  | b - value positioner time constant (sec) (>0.0)
J+14 |  |  |  | c - value positioner feedback
J+15 |  |  |  | Tf - Fuel system time constant (sec)
J+16 |  |  |  | Kf - Fuel system feedback
J+17 |  |  |  | K5 - Radiation shield conduction gain (K4+K5=1)
J+18 |  |  |  | K4 - Radiation shield radiation gain (K4+K5=1)
J+19 |  |  |  | T3 - Radiation shield conduction time constant (sec)(>0.0)
J+20 |  |  |  | T4 - Thermocouple time constant (sec)(>0.0)
J+21 |  |  |  | Ktemp - Temperature control gain (>0.0)
J+22 |  |  |  | T5 - Temperature control time constant (sec)(>0.0)
J+23 |  |  |  | af1 - Fuel influence over exhaust temp (F/pu)
J+24 |  |  |  | bf1 - Speed influence over exhaust temp (F/pu)
J+25 |  |  |  | af2 - Zero fuel power
J+26 |  |  |  | bf2 - Fuel influence over power
J+27 |  |  |  | cf2 - Speed influence over power
J+28 |  |  |  | TR - Rated temperature (F)
J+29 |  |  |  | K6 - Minimum fuel flow (pu)
J+30 |  |  |  | TC - Temperature control set-point (F) (debe ser <= TR)
J+31 |  |  |  | TD - Power measurement time constant
J+32 |  |  |  | P1 - cubic coeff
J+33 |  |  |  | P2 - quadratic coeff
J+34 |  |  |  | P3 - linear coeff
J+35 |  |  |  | P4 - independent coeff
J+36 |  |  |  | Tpwr - Power measure delay
J+37 |  |  |  | DB - Frequency Dead Band
STATEs | # |  | Description |  |  | VARs | # | Description
K |  |  | Speed control P+I |  |  | L |  | Referencia de velocidad
K+1 |  |  | Valve positioner |  |  | L + 1 |  | CSO (salida del control)
K+2 |  |  | Fuel System |  |  | L + 2 |  | Exhaust Temperature (ºF)
K+3 |  |  | Radiation Shield
K+4 |  |  | Thermocouple |  |  | IBUS, 'USRMDL', ID, 'GFT8WX', 5, 0, 0, 38, 12, 3
K+5 |  |  | Temperature control P+I |  |  | CON(J) to CON(J+36) /
K+6 |  |  | Gas Turbine Dynamics
K+7 |  |  | Combustor delay (approx)
K+8 |  |  | Turbine exhaust delay (approx)
K+9 |  |  | Fuel Control delay (approx)
K+10 |  |  | Droop calculation
K+11 |  |  | Power measure delay (approx)
Diagrama de Bloques
GFT8WB
SPEED
PMECH
PELEC