## IEESGO
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
IEESGO: Turbine-Governor Model Data Sheets | [5 empty] | Generador: |  |  |  | Fecha: | Julio 2011
IEEE Standard Model
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VAR starting with |  |  |  |  | L
CONs | # |  | Value | Description
J |  |  |  | T1, controller lag (sec)
J+1 |  |  |  | T2, controller lead compensation (sec)
J+2 |  |  |  | T3, governor lag (>0) (sec)
J+3 |  |  |  | T4, delay due to steam inlet volumes associated with steam chest and inlet piping (sec)
J+4 |  |  |  | T5, reheater delay including hot and cold leads (sec)
J+5 |  |  |  | T6, delay due to IP-LP turbine, crossover pipes, and LP end hoods (sec)
J+6 |  |  |  | K1, 1/per unit regulation
J+7 |  |  |  | K2, fraction
J+8 |  |  |  | K3, fraction
J+9 |  |  |  | PMAX, upper power limit
J+10 |  |  |  | PMIN, lower power limit
STATEs | # |  | Description |  |  |  | VAR | # | Description
K |  |  | Filter output |  |  |  | L |  | Reference, P0
K+1 |  |  | Valve or gate servo output
K+2 |  |  | Turbine powers |  |  |  | IBUS, ’IEESGO’, ID, CON(J) to CON(J+10) /
K+3 |  |  | Turbine powers
K+4 |  |  | Turbine powers
Diagrama de Bloque
IEESGO
SPEED
Speed
PMECH