## TVCC2
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
TVCC2: Turbine-Governor Model Data Sheets | [7 empty] | Generador: |  |  | Fecha: | Julio 2011
Modelo escrito por el Usuario
This model is located at system bus | [5 empty] | IBUS
Machine identifier | [5 empty] | ID
This model uses CONs starting with | [5 empty] | J
and STATEs starting with | [5 empty] | K
and VARs starting with | [5 empty] | L
CONs | # |  | Value | Description |  |  | STATEs |  | # | Description
J |  |  |  | PTOLR |  |  | K |  |  | Salida del Governor
J+1 |  |  |  | QTOLR |  |  | K+1 |  |  | Potencia mecánica sin cambio de base
J+2 |  |  |  | DECAYTM |  |  | K+2 |  |  | Salida de la etapa de baja presión
J+3 |  |  |  | KPFACT |  |  | K+3 |  |  | Posición de la válv. de control de la TV (tcv)
J+4 |  |  |  | PREFMAX |  |  | K+4 |  |  | Salida de la válvula Bypass (tbv)
J+5 |  |  |  | PMULT |  |  | K+5 |  |  | Salida del evaporador de la caldera (tw)
J+6 |  |  |  | BV |  |  | …
J+7 |  |  |  | TBV |  |  | K+8
J+8 |  |  |  | STFRAC |  |  | K+9 |  |  | Salida del Domo de la Caldera (td)
J+9 |  |  |  | R |  |  | …
J+10 |  |  |  | TPELEC |  |  | K+12
J+11 |  |  |  | KP |  |  | K+13 |  |  | Salida del Transductor de PELEC (tpelec)
J+12 |  |  |  | KI |  |  | K+14 |  |  | Salida del control de presión principal
J+13 |  |  |  | VMAX |  |  | K+15 |  |  | Salida del Steam Header (th)
J+14 |  |  |  | VMIN
J+15 |  |  |  | KPP |  |  | IBUS, ‘USRMDL’, ID, ’TVCC2’, 5, 0, 0, 41, 16, 29, CON(J)
J+16 |  |  |  | KIP |  |  | to CON(J+40) /
J+17 |  |  |  | KPG
J+18 |  |  |  | KIG
J+19 |  |  |  | DBD
J+20 |  |  |  | EMAX
J+21 |  |  |  | TW
J+22 |  |  |  | TD
J+23 |  |  |  | TH
J+24 |  |  |  | KL
J+25 |  |  |  | TCV
J+26 |  |  |  | TNRH
J+27 |  |  |  | TDRH
J+28 |  |  |  | Y0
J+29 |  |  |  | X1
J+30 |  |  |  | Y1
J+31 |  |  |  | X2
J+32 |  |  |  | Y2
J+33 |  |  |  | PREFMIN
J+34 |  |  |  | PREFNORM
J+35 |  |  |  | KQV
J+36 |  |  |  | TBASE
J+37 |  |  |  | GT1
J+38 |  |  |  | GT2
J+39 |  |  |  | GT3
J+40 |  |  |  | GT4
VARs | # |  | Description |  | Detalle de las CONs
L |  |  | PT |  | GT1 |  | External bus number of bus at which the plant's gas turbines are connected
L+1 |  |  | PH |  | GT2 |  | External bus number of bus at which the plant's gas turbines are connected
L+2 |  |  | Q11 |  | GT3 |  | External bus number of bus at which the plant's gas turbines are connected
L+3 |  |  | Q22 |  | GT4 |  | External bus number of bus at which the plant's gas turbines are connected
L+4 |  |  | Q33 |  | BV |  | Bypas valve opening in initial condition (normally zero), per unit
L+5 |  |  | Q44 |  | TBV |  | Bypass valve actuator time constnat, seconds
L+6 |  |  | QT |  | STFRAC |  | Single Gas turbine heat output as fraction of steam turbine full load requirement
L+7 |  |  | QB |  | R |  | Steam turbine speed governor droop, per unit
L+8 |  |  | PM |  | TPELEC |  | Steam turbine electrical power transducer time constant, per unit
L+9 |  |  | DQ11 |  | KP |  | Main pressure controller proportional gain
L+10 |  |  | DQ22 |  | KI |  | Main pressure controller integral gain
L+11 |  |  | DQ33 |  | VMAX |  | Maximum steam turbine control valve opening, per unit (not used in the model)
L+12 |  |  | DQ44 |  | VMIN |  | Maximum steam turbine control valve opening, per unit (not used in the model)
L+13 |  |  | NUMGTS |  | KPP |  | Low steam pressure limiter proportional gain
L+14 |  |  | NUMGTBUS |  | KIP |  | Low steam pressure limiter integral gain
L+15 |  |  | COUNT |  | KPG |  | Speed governor proportional gain
L+16 |  |  | GTST11 |  | KIG |  | Speed governor integral gain
L+17 |  |  | GTST22 |  | DBD |  | Speed governor dead band
L+18 |  |  | GTST33 |  | EMAX |  | Maximum speed governor error, per unit
L+19 |  |  | GTST44 |  | TW |  | Boiler evaporator section time constant, seconds
L+20 |  |  | TMR11 |  | TD |  | Boiler drum time constant, seconds
L+21 |  |  | TMR22 |  | TH |  | Steam header time constant, seconds
L+22 |  |  | TMR33 |  | KL |  | Total steam flow pressure loss in superheater and steam header, per unit
L+23 |  |  | TMR44 |  | TCV |  | Steam turbine control valve actuatio time constant, seconds
L+24 |  |  | QFNL11 |  | TNRH |  | Steam turbine reheater model lead time constant, seconds
L+25 |  |  | QFNL22 |  | TDRH |  | Steam turbine reheater model lag time constant, seconds
L+26 |  |  | QFNL33 |  | Y0 |  | Gas turbine heat/power curve zero power intercept, per unit
L+27 |  |  | QFNL44 |  | X1 |  | Gas turbine power coordinate, per unit
L+28 |  |  | REFERENCE |  | Y1 |  | Gas turbine heat coordinate, per unit
[5 empty] | X2 |  | Gas turbine power coordinate, per unit
[5 empty] | Y2 |  | Gas turbine heat coordinate, per unit
[5 empty] | PREFMIN |  | Inlet pressure setpoint, per unit
[5 empty] | PREFNORM |  | Minimum pressure limiter setpoint, per unit
[5 empty] | KQV |  | Steam turbine control valve flow coefficient, per unit (normally 1.0)
Diagrama de Bloques
TVCC2
SPEED Speed
PMECH Power