## UNIABB
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
UNIABB: Excitation System Model Data Sheets | [5 empty] | Generador: |  |  |  | Fecha: | Julio 2011
Modelo escrito por el Usuario
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
ICONs | # |  | Value | Description |  |  | VARs | # | Description
M |  |  |  | SES |  |  | L |  | V/Hz, Comparator Output
M+1 |  |  |  | VCOMP |  |  | L +1 |  | V/Hz, Timer
M+2 |  |  |  | SHUNT |  |  | L +2 |  | V/Hz, Switch control input
M+3 |  |  |  | Set Point 2 |  |  | L +3 |  | V/Hz, Limiter output
M+4 |  |  |  | Off/On OEL Limiter |  |  | L +4 |  | AVR, Setpoint + compensator
M+5 |  |  |  | Off/On UEL Limiter |  |  | L +5 |  | AVR,Utm+LVGate1 output
M+6 |  |  |  | Off/On V/Hz Limiter |  |  | L +6 |  | AVR, HVGate output
M+7 |  |  |  | Off/On Reactive Control |  |  | L +7 |  | AVR, LVGate2 output
Set to 0/1 to disable/enable | [6 empty] | L +8 |  | AVR, Lead-Lag Time Constants selector 2 1
[7 empty] | L +9 |  | AVR, Lead-Lag Time Constants selector 3 1
STATEs | # |  | Description |  |  |  | L +10 |  | AVR, Lead-Lag output
K |  |  | AVR Rectifier |  |  |  | L +11 |  | AVR, Rectifier output
K+1 |  |  | AVR Lead-Lag 1 |  |  |  | L +12 |  | AVR, Rectifier compensated output
K+2 |  |  | AVR Lead-Lag 2 |  |  |  | L +13 |  | AVR, Source voltage for rectifier
K+3 |  |  | AVR Exciter |  |  |  | L +14 |  | MAX IF limiter output
K+4 |  |  | PT Transducer |  |  |  | L +15 |  | IT Limiter Ind output
K+5 |  |  | QT Transducer |  |  |  | L +16 |  | IT Limiter Cap output
K+6 |  |  | FT Transducer |  |  |  | L +17 |  | OEL output
K+7 |  |  | IT Transducer |  |  |  | L +18 |  | Min IF limiter output
K+8 |  |  | IFD Transducer |  |  |  | L +19 |  | UEL output
K+9 |  |  | ECOMP Transducer |  |  |  | L +20 |  | P/Q limiter output
K+10 |  |  | Max IFD limiter integrator |  |  |  | L +21 |  | Compensator output
K+11 |  |  | IT limiter integrator |  |  |  | L +22 |  | Max IF, Comparator 1 output
K+12 |  |  | UT Transducer |  |  |  | L +23 |  | Max IF, Comparator 2 output
K+13 |  |  | Q/V Control |  |  |  | L +24 |  | IT Limiter, Comparator 1 output
K+14 |  |  | Max IF limiter. Filtro P.B. |  |  |  | L +25 |  | IT Limiter, Comparator 2 output
K+15 |  |  | P/Q Limiter. Filtro P.B. |  |  |  | L +26 |  | Crowbar Timer
[7 empty] | L +27 |  | Crowbar Actuated
1 Active Low Logic | [6 empty] | L +28 |  | Qref, Reference of Q/V control 2
2 From Joint Control (CCUNIT model) If ICON(I+7)=1 at UNIABB model and ICON(I)≥0 (Bus Bar Number of ontrolled voltage) at CCUNIT model. Otherwise, Qref is equal to QELEC at initial power flow. | [6 empty] | L +29 |  | S_OEL, OEL Limiter Active 1
[7 empty] | L +30 |  | S_UEL, UEL Limiter Active 1
[7 empty] | L +31 |  | Dead Band Timer On
[7 empty] | L +32 |  | Dead Band Output
IBUS, ‘USRMDL’,ID, ’UNIABB’, 4, 0, 8, 69, 16, 33, ICON(M) to ICON(M+7), CON(J) to CON(J+68) /
CONs | # |  | Value | Description | [6 empty] | *Set any time constant to zero to by-pass lead-lag block.
J |  |  |  | TR, Measuring filter time constant
J+1 |  |  |  | KIR, Reactive power compensation factor
J+2 |  |  |  | KIA, Active power compensation factor
J+3 |  |  |  | KR, Steady state gain
J+4 |  |  |  | TLEAD2_1, Controller second lag time const*
J+5 |  |  |  | TLAG2_1, Controller second lead time const*
J+6 |  |  |  | TLEAD1_1, Controller first lag time constant*
J+7 |  |  |  | TLAG1_1, Controller first lead time constant*
J+8 |  |  |  | TLEAD2_2, Controller second lag time const*
J+9 |  |  |  | TLAG2_2, Controller second lead time const*
J+10 |  |  |  | TLEAD1_2, Controller first lag time const*
J+11 |  |  |  | TLAG1_2, Controller first lead time const*
J+12 |  |  |  | TLEAD2_3, Controller second lag time const*
J+13 |  |  |  | TLAG2_3, Controller second lead time const*
J+14 |  |  |  | TLEAD1_3, Controller first lag time const*
J+15 |  |  |  | TLAG1_3, Controller first lead time const*
J+16 |  |  |  | Up+ AVR Output positive ceiling value
J+17 |  |  |  | Up- AVR Output negative ceiling value
J+18 |  |  |  | KVC AC Side vectorial compounding factor
J+19 |  |  |  | VVCmax Maximum voltage of vectorial compounding
J+20 |  |  |  | KSC, DC series compounding factor
J+21 |  |  |  | VSCmax, Maximum voltage of DC side series compounding
J+22 |  |  |  | Ts, Gate control unit & converter time const.
J+23 |  |  |  | KID, DC-Voltage drop proportional to convert output current
J+24 |  |  |  | TE, Exciter time constant
J+25 |  |  |  | KE, Exciter self excitation factor
J+26 |  |  |  | EF1,
J+27 |  |  |  | SE(EF1)
J+28 |  |  |  | EF2
J+29 |  |  |  | SE(EF2)
J+30 |  |  |  | Efmin, Minimum exciter output voltage
J+31 |  |  |  | KVHZ, Slope of V/Hz limiter
J+32 |  |  |  | U_fn, Frequency for machine voltage=0.0 p.u.
J+33 |  |  |  | Utmax, Max machine voltage
J+34 |  |  |  | T_V_Hz,
J+35 |  |  |  | IFmax1, Setpoint for ceiling field current 1
J+36 |  |  |  | IFmax2, Setpoint for ceiling field current 2
J+37 |  |  |  | IFth1, Setpoint1 for max. Continuos field current
J+38 |  |  |  | IFth2, Setpoint2 for max. Continuos field current
J+39 |  |  |  | KHF, Heating constant field
J+40 |  |  |  | KCF, Cooling constant of field
J+41 |  |  |  | EmaxF, Max. Thermal energy in field
J+42 |  |  |  | KIFmax, Gain reduction factor, Ifmax limiter
J+43 |  |  |  | Itmax, Setpoint for ceiling stator current
J+44 |  |  |  | Itth, Setpoint for max continuos stator current
CONs Continuación…
CONs | # |  | Value | Description
J+45 |  |  |  | KHS, Heating constant of stator winding
J+46 |  |  |  | KCS, Cooling constant of stator winding
J+47 |  |  |  | EmaxS, Max thermal energy in stator
J+48 |  |  |  | KITind, Gain reduction factor for Stator current limiter inductive
J+49 |  |  |  | KITcap, Gain reduction factor for Stator current limiter capacitive
J+50 |  |  |  | Ifmin, Minimum field current limit setpoint
J+51 |  |  |  | KIFmin, Gain reduction factor, Ifmin limiter
J+52 |  |  |  | X1, P/Q limiter-Table input 1
J+53 |  |  |  | F(X1), P/Q limiter-Table output 1
J+54 |  |  |  | X2, P/Q limiter-Table input 2
J+55 |  |  |  | F(X2), P/Q limiter-Table output 2
J+56 |  |  |  | X3, P/Q limiter-Table input 3
J+57 |  |  |  | F(X3), P/Q limiter-Table output 3
J+58 |  |  |  | X4, P/Q limiter-Table input 4
J+59 |  |  |  | F(X4), P/Q limiter-Table output 4
J+60 |  |  |  | X5, P/Q limiter-Table input 5
J+61 |  |  |  | F(X5), P/Q limiter-Table output 5
J+62 |  |  |  | KPQ, Gain reduction factor for P/Q limiter
J+63 |  |  |  | rd/rfd
J+64 |  |  |  | TQ, Time constant of Q/V controller
J+65 |  |  |  | Lsup, Up limit of Q/V controller
J+66 |  |  |  | LInf, Down limit of Q/V controller
J+67 |  |  |  | Dead Band, Dead Band of Q/V controller
J+68 |  |  |  | Timer On, Delay Time for error out of Dead Band in Q/V controller
Diagrama de Bloques |  |  |  |  | Control Conjunto de Tensión
UNIABB
VTRM
EFD
ECOMP
PELEC
QELEC
FREC
ITRM