## VWEX1
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
VWEX1: Wind Turbine Dynamic Stability Model | [5 empty] | Generador: | Fecha: | Mayo 2013
Modelo escrito por el Usuario: Vestas Wind Turbine Generator Voltage Control
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
ICONs | # |  | Value | Description
M |  |  |  | 1 for Q control, 2 for PF control, 3 for voltage Droop control and 4 for voltage PI control
M+1 |  |  |  | WTG type: 1 V80-2MW-VCS-MK7 2 V80-2MW-VCUS-MK7 3 V90-2MW-VCS-MK7 4 V90-3MW-VCS-MK9 5 V90-3N1W-VCRS-MK9 6 V112-3MW-50/60Hz-MK9
M+2 |  |  |  | Internal use
M+3 |  |  |  | Internal use
M+4 |  |  |  | Not in use
M+5 |  |  |  | PCC bus number
M+6 |  |  |  | Capacitor bank/Stacom bus number
M+7 |  |  |  | Vestas option: 1 for WTG control, 2 for WTG and capacitor bank control and 3 WTG and stacom control
M+8 |  |  |  | Internal use
M+9 |  |  |  | Internal use
M+10 |  |  |  | Internal use
M+11 |  |  |  | Internal use
M+12 |  |  |  | Internal use
M+13 |  |  |  | Plant controller activation
M+14 |  |  |  | Internal use
M+15 |  |  |  | Internal use
M+16 |  |  |  | Internal use
M+17 |  |  |  | Internal use
M+18 |  |  |  | Internal use
M+19 |  |  |  | Internal use
M+20 |  |  |  | PPC circuit from Bus
M+21 |  |  |  | PPC circuit To Bus
M+22 |  |  |  | PPC circuit ID
CONs | # |  | Value | Description
J |  |  |  | Time constant for PCC voltage measurement
J+1 |  |  |  | Dead band for Voltage Controller, pu
J+2 |  |  |  | QAVACAP: pu in WTG base
J+3 |  |  |  | QAVAIND: pu in WTG base
J+4 |  |  |  | Droop in percentage for voltage PI controller (e.g. 5)
J+5 |  |  |  | Time constant for P measurement
J+6 |  |  |  | Time constant for Q measurement
J+7 |  |  |  | Dead band for reactive power controller (pu in WTG MVA base)
J+8 |  |  |  | KGS1
J+9 |  |  |  | SCR
J+10 |  |  |  | XpR
J+11 |  |  |  | Kp for WTG Type 123
J+12 |  |  |  | Ti for WTG Type 123
J+13 |  |  |  | Kp for WTG Type 45
J+14 |  |  |  | Ti for WTG Type 45
J+15 |  |  |  | Kp for WTG Type 6
J+16 |  |  |  | Ti for WTG Type 6
J+17 |  |  |  | VolHiPCC in FRT controller, pu
J+18 |  |  |  | VolLoPCC in FRT controller
J+19 |  |  |  | STACOM cap capacity, pu in 100 MVA base
J+20 |  |  |  | STACOM ind capacity, pu in 100 MVA base
J+21 |  |  |  | Freeze wait time in seconds
J+22 |  |  |  | Cap_off_voltage
J+23 |  |  |  | Post-fault time in seconds
J+24 |  |  |  | Cap_off_time
J+25 |  |  |  | PPC Signal Delay to capacitor Bank
J+26 |  |  |  | PPC Signal Delay to WTG/STACOM
J+27 |  |  |  | Not in use
STATEs | # |  | Description
K |  |  | PCC Voltage Measurement
K+1 |  |  | PCC P measurement, pu in Machine base
K+2 |  |  | PCC Q measurement, pu in Machine base
K+3 |  |  | Integrator in reactive power controller
K+4 |  |  | Integrator in voltage PI controller
K+5 |  |  | Not in use
K+6 |  |  | Cap_off_timer
VARs | # |  | Description
L |  |  | Q setting, pu in tnachine base
L+1 |  |  | Q set pf
L+2 |  |  | Q set droop
L+3 |  |  | PF setting
L+4 |  |  | Voltage setting at PCC
L+5 |  |  | Q reference after limiter
L+6 |  |  | Dead band in Reactive power controller
L+7 |  |  | Gain Kp in Reactive Power controller
L+8 |  |  | Saturation input in Reactive Power controller
L+9 |  |  | Qref in Reactive Power controller
L+10 |  |  | Gain 1/Ti in Reactive Power controller
L+11 |  |  | Sample and Hold in Reactive Power controller
L+12 |  |  | Stacom output in system MVA base
L+13 |  |  | Dead band in Voltage PI controller
L+14 |  |  | Gain Kp in Voltage PI controller
L+15 |  |  | Saturation input in Voltage PI Controller
L+16 |  |  | Qref in Voltage PI controller
L+17 |  |  | Gain 1/Ti in Voltage PI controller
L+18 |  |  | Sample and Hold in Voltage PI controller
L+19 |  |  | Qref in Selection 2
L+20 |  |  | For CB delay
L+21 |  |  | Capacitor bank B capacity in system MVA base
L+22 |  |  | Capacity bank B output in system MVA base
L+23 |  |  | Internal use
L+24 |  |  | Internal use
L+25 |  |  | PPC Delay to WIG
L+26 |  |  | PPC Delay to STACOM
L+27 |  |  | Memory for Delay from PPC to WTG
…
L+40
L+41 |  |  | Internal use
L+42 |  |  | Internal use
L+43 |  |  | Not in use
…
L+55
L+56 |  |  | PPC circuit MW
L+57 |  |  | PPC circuit Mvar
L+58 |  |  | PPC circuit MVA
All power quantities are in per unit on the machine base. Slope limits are in p.u. per second. Vref: Q signal to WTG
IBUS, ‘USRMDL’, ID, ’VWEX1’, 4, 0, 23, 28, 7, 59, ICON(M) to ICON(M+22), CON(J) to CON(J+27) /