## VWGOV
CAMMESA – GERENCIA ESTUDIOS ELÉCTRICOS BIBLIOTECA DE MODELOS PSS/E
VWGOV: Wind Turbine Dynamic Stability Model | [5 empty] | Generador: |  |  | Fecha: | Mayo 2013
Modelo escrito por el Usuario: Vestas Wind Turbine Generator Governor
This model is located at system bus |  |  |  |  | IBUS
Machine identifier |  |  |  |  | ID
This model uses CONs starting with |  |  |  |  | J
and STATEs starting with |  |  |  |  | K
and VARs starting with |  |  |  |  | L
and ICONs starting with |  |  |  |  | M
ICONs | # |  | Value | Description
M |  |  |  | 1 for Power Control 2 for FSM 3 for LFSM
M+1 |  |  |  | From bus
M+2 |  |  |  | To Bus
M+3 |  |  |  | Circuit ID
M+4 |  |  |  | Internal Use
CONs | # |  | Value | Description
J |  |  |  | FqUpDB_FSM: Hz
J+1 |  |  |  | FqDwDB_FSM: Hz
J+2 |  |  |  | FqUpDB_LFSM: Hz
J+3 |  |  |  | FqDwDB_LFSM: Hz
J+4 |  |  |  | FqSlopOver_FSM: Droop % in df/dpg
J+5 |  |  |  | FqSlopUncler_FSM: Droop % in df/dpg
J+6 |  |  |  | FqSlopOver_LFSM: Droop % in df/dpg
J+7 |  |  |  | FqSlopUncier_LFSM: Droop % in df/dpg
J+8 |  |  |  | PPC signal delay to WTG
J+9 |  |  |  | PRamplimiter: pu/second
J+10 |  |  |  | Plimit, pu
J+11 |  |  |  | PminWPP. pu
J+12 |  |  |  | RatedPower, pu
J+13 |  |  |  | Kapc
VARs | # |  | Description |  |  | STATEs | # | Description
L |  |  | Pcurtail in pu |  |  | K |  | PRampLimiter in freq response
L+1 |  |  | Frequency setting in Hz |  |  | K+1 |  | PRampRate
L+2 |  |  | Pset, PPC power flow |  |  | K+2 |  | Freq filter
L+3 |  |  | df / f *(100/Slope) |  |  | K+3 |  | Rate Limiter in Power Control
L+4 |  |  | (L+3)* Fq Selector |  |  | K+4 |  | Pmeas
L+5 |  |  | Min |  |  | K+5 |  | Pwtgs
L+6 |  |  | Saturation Dynamic
L+7 |  |  | Pref |  |  | All power quantities are in per unit on the machine base. Slope limits are in p.u. per second.
L+8 |  |  | OverFrequency Flag
L+9 |  |  | Memory
L+10 |  |  | Memory and Selection |  |  | IBUS, ‘USRMDL’, ID, ’VWGOV’, 5, 0, 5, 14, 6, 45,
L+11 |  |  | Delayed Output |  |  | ICON(M) to ICON(M+4), CON(J) to CON(J+13) /
L+12
… |  |  | Internal Use
L+25
L+26 |  |  | Df in Hz
L+27 |  |  | Limiter in Power Control
L+28 |  |  | Power Flow
L+29 |  |  | Reactive Power Flow
L+30 |  |  | S Flow
L+31 |  |  | Variable after Kpac
L+32 |  |  | Var(L+31) add up to Pwtgs
L+33 |  |  | Active Power dispatch
L+34 |  |  | Input to state (k)
L+35 |  |  | Sampled Pmeas
L+36 |  |  | Sampled Pwtgs
L+37 |  |  | Sampled Freq measurement
L+38 |  |  | Sampled Pset
L+39 |  |  | Sampled Freeze signal
L+40 |  |  | Sampled Pcurtil
L+41 |  |  | Sampled Feq Setting
L+42 |  |  | Sample Active
L+43 |  |  | Not in use
L+44 |  |  | PPC activated